Things To Do When System 21 Crashes, Hangs, etc.

- If an M21 “crashes”, note the condition of the 2nd and 3rd LED on the M21 (LEDs 7 & 8). If the 3rd LED is flashing steadily, then the M21 is still operating as far as it’s concerned. If the bottom LED is flashing, then the M21 is taking readings from the sensor (1 blink every 50 measurements). If the 3rd and 4th LEDs are on solid (top may be blinking, rest off) the M21 is in BOOT mode and is trying to reload itself. The standard startup LED patterns also denote that the M21 has rebooted.

- If an M21 rebooted itself, check to see if there is new information in the crashdmp.dat file in the F:\bootp directory. When an M21 crashes in a controlled manner, it saves register and program information into non-volatile RAM. When the M21 is running again, it appends this information to the crashdmp.dat file. If the M21 crashes in an uncontrolled manner (hard power loss, etc.) no log is created. Also if the M21 is replaced, the saved data is not copied to the PC since the M21 has been removed.

- If an M21 attempts to reboot for any reason, manual or automatic, the fact that it loading is logged in the F:\TFTPBOOT\TFTP.Log file. If the attempt to reboot fails, there may be information in this file that the load failed. If the file logs that the file was transmitted, then the load failure is not due to TFTP

- OPC Server status – Click on the different M21 names in the left-middle of the server. On the Right half the variables for that M21 will be displayed. The first variable is the heartbeat. Is it changing? Is the variable status GOOD, COMMUNICATION FAILURE, or something else? If the heartbeat is changing, the M21 is running and communicating with the PC. If the OPC Server is slow to respond to changes, it has probably lost communications with one or more M21. This will cause the Server to spend a large portion of the CPU time trying to talk to the M21, leading to degraded performance in general. A down M21 can be removed from the server by right-clicking the M21 name. This will pop up a menu that allows the M21 to be “Removed From Service”. When the M21 has been restored, it can be put back into service by again right clicking the M21 name and Putting it In Service.

- Wonderware status:

  - What is the Frame status for each scanner on the top of the display? (OFFSHEET, SCANNING, etc.). Is it Blinking? (indicates lost communication with the corresponding M21). What about the Control status labels?

  - Is the Comm Status LED red, green or yellow? If it’s red, look at the Diagnostic Trend (Misc. Menu). It should show the comm counter for each M21 in a different color. To determine which color is which M21, click on the trend, it will bring up the trend configurator, which will show the variables and their colors.